## 1 PHASE
[5 empty] | PANEL: | 200 |  | MEMBER NAME: |  | HWEC EXAMPLE
[5 empty] | MAIN (A): | 200 |  | SERVICE ADDRESS: |  | 1399 BUSINESS PARK DR S
[5 empty] | VOLTS: | 120 / 240 |  |  |  | NORTH BALTIMORE, OH 45840
[5 empty] | PHASES | 1
LOAD DESCRIPTION |  | VOLT AMPS | POLES | CKT. BRK. | A | B | CKT. BRK. | POLES | VOLT AMPS | LOAD DESCRIPTION
1 | RECEPTACLE | 1080 | 1 | 20 | 2880 |  | 20 | 1 | 1800 | REFRIGERATOR | 2
3 | RECEPTACLE | 1080 | 1 | 20 |  | 4220 | 30 | 2 | 6280 | STOVE | 4
5 | RECEPTACLE | 1080 | 1 | 20 | 4220 | [5 empty] | 6
7 | LIGHTS | 300 | 1 | 20 |  | 800 | 20 | 1 | 500 | LIGHTS | 8
9 | LIGHTS | 300 | 1 | 20 | 800 |  | 20 | 1 | 500 | LIGHTS | 10
11 | HVAC | 8000 | 2 | 40 |  | 4345.5 | 20 | 2 | 691 | MOTOR 1 (3/4HP) | 12
13 |  |  |  |  | 4345.5 | [5 empty] | 14
15 | [10 empty] | 16
17 | [10 empty] | 18
19 | [10 empty] | 20
21 | [10 empty] | 22
23 | [10 empty] | 24
25 | [10 empty] | 26
27 | [10 empty] | 28
29 | [10 empty] | 30
31 | [10 empty] | 32
33 | [10 empty] | 34
35 | [10 empty] | 36
37 | [10 empty] | 38
39 | [10 empty] | 40
41 | [10 empty] | 42
43 | [10 empty] | 44
45 | [10 empty] | 46
[5 empty] | 12245.5 | 9365.5
LOAD CLASSIFICATION |  | CONNECTED (VA) |  | DEMAND FACTOR (%) |  | ESTIMATED DEMAND (VA) |  | PANEL TOTALS
LIGHTING |  | 1600 |  | 100% |  | 1600 |  | 21611 |  | : TOTAL CONNECTED LOAD (VA)
GENERAL RECEPTICLE |  | 3240 |  | 50% |  | 1620 |  | 15991 |  | : TOTAL EST. DEMAND (VA)
DEDICATED RECEPTICLE |  | 8080 |  | 100% |  | 8080 |  | 90.0458 |  | : TOTAL CONNECTED AMPS
HVAC |  | 8000 |  | 50% |  | 4000 |  | 66.6292 |  | : TOTAL EST. DEMAND AMPS
MOTORS (NOT INCLUDING LARGEST) |  |  |  | 50%
LARGEST MOTOR |  | 691 |  | 100% |  | 691
OTHER

## 3 PHASE
[5 empty] | PANEL: | 1 |  |  | MEMBER NAME: |  | HWEC EXAMPLE
[5 empty] | MAIN (A): | 200 |  |  | SERVICE ADDRESS: |  | 1399 BUSINESS PARK DR S
[5 empty] | VOLTS: | 120 / 208 |  |  |  |  | NORTH BALTIMORE, OH 45840
[5 empty] | PHASES | 3
LOAD DESCRIPTION |  | VOLT AMPS | POLES | CKT. BRK. | A | B | C | CKT. BRK. | POLES | VOLT AMPS | LOAD DESCRIPTION
1 | MOTOR 1 (5HP) | 5040 | 3 | 20 | 4346.6667 |  |  | 30 | 3 | 8000 | HVAC | 2
3 | [5 empty] | 4346.6667 | [5 empty] | 4
5 | [6 empty] | 4346.6667 |  |  |  |  | 6
7 | RECEPTACLE | 1080 | 1 | 20 | 2880 |  |  | 20 | 1 | 1800 | REFRIGERATOR | 8
9 | RECEPTACLE | 1080 | 1 | 20 |  | 4220 |  | 40 | 2 | 6280 | STOVE | 10
11 | RECEPTACLE | 1080 | 1 | 20 |  |  | 4220 | 40 |  |  |  | 12
13 | LIGHTS | 300 | 1 | 20 | 800 |  |  | 20 | 1 | 500 | LIGHTS | 14
15 | LIGHTS | 300 | 1 | 20 |  | 800 |  | 20 | 1 | 500 | LIGHTS | 16
17 | MOTOR 2 (10HP) | 10080 | 3 | 40 | 3360 |  |  | 30 | 3 |  | SPARE | 18
19 | [5 empty] | 3360 | [5 empty] | 20
21 | [6 empty] | 3360 |  |  |  |  | 22
23 | [11 empty] | 24
25 | [11 empty] | 26
27 | [11 empty] | 28
29 | [11 empty] | 30
31 | [11 empty] | 32
33 | [11 empty] | 34
35 | [11 empty] | 36
37 | [11 empty] | 38
39 | [11 empty] | 40
41 | [11 empty] | 42
[5 empty] | 11386.6667 | 12726.6667 | 11926.6667
LOAD CLASSIFICATION |  | CONNECTED (VA) |  | DEMAND FACTOR (%) |  | ESTIMATED DEMAND (VA) |  |  | PANEL TOTALS
LIGHTING |  | 1600 |  | 100% |  | 1600 |  |  | 36040 | 36040 | : TOTAL CONNECTED LOAD (VA)
GENERAL RECEPTICLE |  | 3240 |  | 50% |  | 1620 |  |  | 27900 | 27900 | : TOTAL EST. DEMAND (VA)
DEDICATED RECEPTICLE |  | 8080 |  | 100% |  | 8080 |  |  | 173.2692 | 173.2692 | : TOTAL CONNECTED (A)
HVAC |  | 8000 |  | 50% |  | 4000 |  |  | 134.1346 | 134.1346 | : TOTAL EST. DEMAND (A)
MOTORS (NOT INCLUDING LARGEST) |  | 5040 |  | 50% |  | 2520
LARGEST MOTOR |  | 10080 |  | 100% |  | 10080
OTHER

## INPUT DATA
VOLTAGE | CKT BRK.
120 / 240 | 10
120 / 208 | 15
277 / 480 | 20
25
30
35
40
45
50
60
70
80
90
100
110
125
150
175
200
225
250
300
320
350
400
450
500
600
700
800
1000
1200
1600
2000